## data
Quarter | Year | Brand name | Brand logo | Region | Unit photo | Unit name | Unit type | Execution | Unit size quantity | Eurovent Certificate | Eurovent Model Box | Casing Strength (Eurovent) | Casing leakage, negative pressure (Eurovent) | Casing leakage, positive pressure (Eurovent) | Filter mounting leakage (Eurovent) | Thermal isolation (Eurovent) | Thermal bridges (Eurovent) | VDI 6022-1 certification | Supply | Exhaust | Supply/Exhaust without recovery | Supply/Exhaust with RRG | Supply/Exhaust with PCR (HEX) | Supply/Exhaust with glycol | Insulation material | Insulation thickness [mm] | Metal sheet (Internal) | Metal sheet thickness (Internal) [mm] | Metal sheet (External) | Metal sheet thickness (External) [mm] | Unit size | Recovery type | Minimum airflow [CMH] | Maximum airflow (CCOL) [CMH] | Optimal airflow (ErP2018) [CMH] | Air speed on Filter at opt airflow (ErP) [m/s] | Internal Width (Supply Filter) [mm] | Internal Height (Supply Filter) [mm] | Unit cross section area (Supply Filter) [m2] | Internal Width (Supply Fan) [mm] | Internal Height (Supply Fan) [mm] | x1 | x2 | x3 | x4 | x5 | y1 | y2 | y3 | y4 | y5 | x6 | x7 | x8 | x9 | x10 | y6 | y7 | y8 | y9 | y10 | Unit cross section area (Supply Fan) [m2] | Duct connection Width [mm] | Duct connection Height [mm] | x11 | x12 | x13 | x14 | x15 | y11 | y12 | y13 | y14 | y15 | Duct connection Diameter [mm] | Type | Wheel diameter [mm] | Distance between lamels [mm] | Sens. efficiency at nominal balanced airflows_RRG [%] | Sens. efficiency at opt balanced airflows (ErP)_RRG [%] | Material | Sens. efficiency at nominal balanced airflows_PCR/HEX [%] | Sens. efficiency at opt balanced airflows (ErP)_PCR/HEX [%] | Motor type | Motor quantity | Motor rated power [kW] | Impeller size (available optins) | Impeller efficiency at optimal airflow [%] | Heating elements type | Capacity range1 [kW] | Capacity range2 [kW] | Capacity range3 [kW] | Capacity Note | Water heater_min rows | Water heater_max rows | Water cooler_min rows | Water cooler_max rows | DXH_min rows | DXH_max rows | DXH sections range | Available refrigerant types | Filter type_Supply | Filtration class_Supply | Filtration efficiency_Supply | Initial PD at nominal airflow_Supply | Final PD_Supply | Filter type_Exhaust | Filtration class_Exhaust | Filtration efficiency_Exhaust | Initial PD at nominal airflow_Exhaust | Final PD_Exhaust | Silencer casing | Base frame/Feets height [mm] | Cabling
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR20 | RRG | 421 | 2185 | 1740 | 2.1 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | NH.RRG | 590 | 1.4 | N/A | 76.5 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 143 | 353 | Bag | ePM10 | 60 | 99 | 297 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR20 | RRG | 421 | 2185 | 1650 | 2 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Total | 590 | 1.4 | N/A | 75.1 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 143 | 353 | Bag | ePM10 | 60 | 99 | 297 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC20 | HEX | 421 | 2185 | 1740 | 2.1 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 86.5 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 143 | 353 | Bag | ePM10 | 60 | 99 | 297 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR25 | RRG | 590 | 2614 | 2050 | 1.9 | 765 | 468.5 | 0.3584 | 765 | 468.5 | 0 | 0 | 765 | 765 | 0 | 0 | 468.5 | 468.5 | 0 | 0 | 0 | 0 | 765 | 765 | 0 | 0 | 468.5 | 468.5 | 0 | 0 | 0.3584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | NH.RRG | 700 | 1.4 | N/A | 78.5 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 100 | 273 | Bag | ePM10 | 60 | 64 | 191 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR25 | RRG | 590 | 2614 | 2050 | 1.9 | 765 | 780 | 0.5967 | 466 | 780 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Total | 700 | 1.4 | N/A | 76.9 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 100 | 273 | Bag | ePM10 | 60 | 64 | 191 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC25 | HEX | 590 | 2614 | 2000 | 1.9 | 765 | 780 | 0.5967 | 466 | 780 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 87.1 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 100 | 273 | Bag | ePM10 | 60 | 64 | 191 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR35 | RRG | 760 | 4097 | 3100 | 2.2 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 793 | 1.4 | N/A | 76.4 | 0 | 0 | 0 | EC | 1 | 1.3 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 82 | 246 | Bag | ePM10 | 60 | 58 | 173 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR35 | RRG | 760 | 4097 | 3100 | 2.2 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 793 | 1.4 | N/A | 74.1 | 0 | 0 | 0 | EC | 1 | 1.3 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 82 | 246 | Bag | ePM10 | 60 | 58 | 173 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC35 | HEX | 760 | 4097 | 3100 | 2.2 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.1 | EC | 1 | 1.3 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 82 | 246 | Bag | ePM10 | 60 | 58 | 173 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR50 | RRG | 1102 | 4968 | 3700 | 2 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 950 | 1.4 | N/A | 78.8 | 0 | 0 | 0 | EC | 1 | 1.35 | N/A | N/A | Tubular | 3.5 | 7.1 | 10.4 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 79 | 226 | Bag | ePM10 | 60 | 41 | 123 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR50 | RRG | 1102 | 4968 | 3700 | 2 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 950 | 1.4 | N/A | 77.2 | 0 | 0 | 0 | EC | 1 | 1.35 | N/A | N/A | Tubular | 3.5 | 7.1 | 10.4 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 79 | 226 | Bag | ePM10 | 60 | 41 | 123 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC50 | HEX | 1102 | 4968 | 3600 | 1.6 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.4 | EC | 1 | 1.35 | N/A | N/A | Tubular | 3.5 | 7.1 | 10.4 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 79 | 226 | Bag | ePM10 | 60 | 41 | 123 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR70 | RRG | 1480 | 6862 | 6300 | 1.8 | 1186 | 677 | 0.80292 | 1186 | 677 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0.80292 | 800 | 400 | 0 | 0 | 800 | 800 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 1100 | 1.4 | N/A | 79.6 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR70 | RRG | 1480 | 6862 | 6300 | 1.8 | 1186 | 677 | 0.80292 | 1186 | 677 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0.80292 | 800 | 400 | 0 | 0 | 800 | 800 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 1100 | 1.4 | N/A | 73 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC70 | HEX | 1480 | 6862 | 5400 | 1.7 | 1186 | 677 | 0.80292 | 1186 | 677 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0.80292 | 800 | 400 | 0 | 0 | 800 | 800 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.2 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR15 | RRG | 421 | 1429 | 1100 | 1.3 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | NH.RRG | 590 | 1.4 | N/A | 80.9 | 0 | 0 | 0 | EC | 1 | 0.36 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 173 | Bag | ePM10 | 60 | 48 | 145 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR15 | RRG | 421 | 1429 | 1100 | 1.3 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Total | 590 | 1.4 | N/A | 80.5 | 0 | 0 | 0 | EC | 1 | 0.36 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 173 | Bag | ePM10 | 60 | 48 | 145 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR30 | RRG | 760 | 3125 | 2350 | 1.7 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 793 | 1.4 | N/A | 79.6 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 53 | 160 | Bag | ePM10 | 60 | 37 | 112 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR30 | RRG | 760 | 3125 | 2350 | 1.7 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 793 | 1.4 | N/A | 78.5 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 53 | 160 | Bag | ePM10 | 60 | 37 | 112 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR60 | RRG | 1102 | 6235 | 4545 | 2.4 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 950 | 1.4 | N/A | 76.6 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 110 | 313 | Bag | ePM10 | 60 | 57 | 171 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR60 | RRG | 1102 | 6235 | 4545 | 2.4 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 950 | 1.4 | N/A | 74.2 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 110 | 313 | Bag | ePM10 | 60 | 57 | 171 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR80 | RRG | 2070 | 7538 | 6200 | 1.8 | 1386 | 777.5 | 1.0776 | 1386 | 777.5 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 1.0776 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | NH.RRG | 1300 | 1.4 | N/A | 79.9 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 5.2 | 12.3 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 67 | 190 | Bag | ePM10 | 60 | 39 | 118 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR80 | RRG | 2070 | 7538 | 6200 | 1.8 | 1386 | 777.5 | 1.0776 | 1386 | 777.5 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 1.0776 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Total | 1300 | 1.4 | N/A | 78.7 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 5.2 | 12.3 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 67 | 190 | Bag | ePM10 | 60 | 39 | 118 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC30 | HEX | 760 | 3125 | 2350 | 1.7 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.8 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO | 120 | Factory wired
Q1 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC60 | HEX | 1102 | 6235 | 4450 | 2 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 87.7 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR20 | RRG | 421 | 2185 | 1740 | 2.1 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | NH.RRG | 590 | 1.4 | N/A | 76.5 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 143 | 353 | Bag | ePM10 | 60 | 99 | 297 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR20 | RRG | 421 | 2185 | 1650 | 2 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Total | 590 | 1.4 | N/A | 75.1 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 143 | 353 | Bag | ePM10 | 60 | 99 | 297 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC20 | HEX | 421 | 2185 | 1740 | 2.1 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 86.5 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 143 | 353 | Bag | ePM10 | 60 | 99 | 297 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR25 | RRG | 590 | 2614 | 2050 | 1.9 | 765 | 468.5 | 0.3584 | 765 | 468.5 | 0 | 0 | 765 | 765 | 0 | 0 | 468.5 | 468.5 | 0 | 0 | 0 | 0 | 765 | 765 | 0 | 0 | 468.5 | 468.5 | 0 | 0 | 0.3584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | NH.RRG | 700 | 1.4 | N/A | 78.5 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 100 | 273 | Bag | ePM10 | 60 | 64 | 191 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR25 | RRG | 590 | 2614 | 2050 | 1.9 | 765 | 780 | 0.5967 | 466 | 780 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Total | 700 | 1.4 | N/A | 76.9 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 100 | 273 | Bag | ePM10 | 60 | 64 | 191 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC25 | HEX | 590 | 2614 | 2000 | 1.9 | 765 | 780 | 0.5967 | 466 | 780 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0 | 0 | 780 | 780 | 0 | 0 | 466 | 466 | 0 | 0 | 0.5967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 87.1 | EC | 1 | 0.78 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 100 | 273 | Bag | ePM10 | 60 | 64 | 191 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR35 | RRG | 760 | 4097 | 3100 | 2.2 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 793 | 1.4 | N/A | 76.4 | 0 | 0 | 0 | EC | 1 | 1.3 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 82 | 246 | Bag | ePM10 | 60 | 58 | 173 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR35 | RRG | 760 | 4097 | 3100 | 2.2 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 793 | 1.4 | N/A | 74.1 | 0 | 0 | 0 | EC | 1 | 1.3 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 82 | 246 | Bag | ePM10 | 60 | 58 | 173 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC35 | HEX | 760 | 4097 | 3100 | 2.2 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.1 | EC | 1 | 1.3 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 82 | 246 | Bag | ePM10 | 60 | 58 | 173 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR50 | RRG | 1102 | 4968 | 3700 | 2 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 950 | 1.4 | N/A | 78.8 | 0 | 0 | 0 | EC | 1 | 1.35 | N/A | N/A | Tubular | 3.5 | 7.1 | 10.4 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 79 | 226 | Bag | ePM10 | 60 | 41 | 123 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR50 | RRG | 1102 | 4968 | 3700 | 2 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 950 | 1.4 | N/A | 77.2 | 0 | 0 | 0 | EC | 1 | 1.35 | N/A | N/A | Tubular | 3.5 | 7.1 | 10.4 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 79 | 226 | Bag | ePM10 | 60 | 41 | 123 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC50 | HEX | 1102 | 4968 | 3600 | 1.6 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.4 | EC | 1 | 1.35 | N/A | N/A | Tubular | 3.5 | 7.1 | 10.4 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 79 | 226 | Bag | ePM10 | 60 | 41 | 123 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR70 | RRG | 1480 | 6862 | 6300 | 1.8 | 1186 | 677 | 0.80292 | 1186 | 677 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0.80292 | 800 | 400 | 0 | 0 | 800 | 800 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 1100 | 1.4 | N/A | 79.6 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR70 | RRG | 1480 | 6862 | 6300 | 1.8 | 1186 | 677 | 0.80292 | 1186 | 677 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0.80292 | 800 | 400 | 0 | 0 | 800 | 800 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 1100 | 1.4 | N/A | 73 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC70 | HEX | 1480 | 6862 | 5400 | 1.7 | 1186 | 677 | 0.80292 | 1186 | 677 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0 | 0 | 1186 | 1186 | 0 | 0 | 677 | 677 | 0 | 0 | 0.80292 | 800 | 400 | 0 | 0 | 800 | 800 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.2 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR15 | RRG | 421 | 1429 | 1100 | 1.3 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | NH.RRG | 590 | 1.4 | N/A | 80.9 | 0 | 0 | 0 | EC | 1 | 0.36 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 173 | Bag | ePM10 | 60 | 48 | 145 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR15 | RRG | 421 | 1429 | 1100 | 1.3 | 650 | 418.5 | 0.27203 | 650 | 418.5 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0 | 0 | 650 | 650 | 0 | 0 | 418.5 | 418.5 | 0 | 0 | 0.27203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Total | 590 | 1.4 | N/A | 80.5 | 0 | 0 | 0 | EC | 1 | 0.36 | N/A | N/A | Tubular | 5.2 | 0 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 173 | Bag | ePM10 | 60 | 48 | 145 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR30 | RRG | 760 | 3125 | 2350 | 1.7 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 793 | 1.4 | N/A | 79.6 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 53 | 160 | Bag | ePM10 | 60 | 37 | 112 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR30 | RRG | 760 | 3125 | 2350 | 1.7 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 793 | 1.4 | N/A | 78.5 | 0 | 0 | 0 | EC | 1 | 0.78 | N/A | N/A | Tubular | 3.5 | 7.1 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 53 | 160 | Bag | ePM10 | 60 | 37 | 112 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR60 | RRG | 1102 | 6235 | 4545 | 2.4 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | 950 | 1.4 | N/A | 76.6 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 110 | 313 | Bag | ePM10 | 60 | 57 | 171 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR60 | RRG | 1102 | 6235 | 4545 | 2.4 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Total | 950 | 1.4 | N/A | 74.2 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 110 | 313 | Bag | ePM10 | 60 | 57 | 171 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR80 | RRG | 2070 | 7538 | 6200 | 1.8 | 1386 | 777.5 | 1.0776 | 1386 | 777.5 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 1.0776 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | NH.RRG | 1300 | 1.4 | N/A | 79.9 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 5.2 | 12.3 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 67 | 190 | Bag | ePM10 | 60 | 39 | 118 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 9 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SR80 | RRG | 2070 | 7538 | 6200 | 1.8 | 1386 | 777.5 | 1.0776 | 1386 | 777.5 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 0 | 0 | 1386 | 1386 | 0 | 0 | 777.5 | 777.5 | 0 | 0 | 1.0776 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Total | 1300 | 1.4 | N/A | 78.7 | 0 | 0 | 0 | EC | 1 | 2.1 | N/A | N/A | Tubular | 5.2 | 12.3 | 0 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 67 | 190 | Bag | ePM10 | 60 | 39 | 118 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC30 | HEX | 760 | 3125 | 2350 | 1.7 | 858 | 525.5 | 0.45088 | 858 | 525.5 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0 | 0 | 858 | 858 | 0 | 0 | 525.5 | 525.5 | 0 | 0 | 0.45088 | 500 | 400 | 0 | 0 | 500 | 500 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 88.8 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO | 120 | Factory wired
Q2 | 2025 | Systemair | Systemair.png | CER | Topvex.png | Topvex | Compact | Floor-mounted | 7 | YES | Compact | D2 | L2 | L2 | F9 | T2 | TB2 | NO | NO | NO | NO | YES | YES | NO | MW | 50 | ZnMg | 0.7 | ZnMg | 0.7 | SC60 | HEX | 1102 | 6235 | 4450 | 2 | 1028 | 602.5 | 0.61937 | 1028 | 602.5 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0 | 0 | 1028 | 1028 | 0 | 0 | 602.5 | 602.5 | 0 | 0 | 0.61937 | 700 | 400 | 0 | 0 | 700 | 700 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | AL | N/A | 87.7 | EC | 1 | 2.1 | N/A | N/A | Tubular | 3.5 | 10.4 | 14.2 |  | 1 | 2 | 2 | 6 | 2 | 6 | 1 | R410A, R407C, R32 | Bag | ePM1 | 60 | 70 | 194 | Bag | ePM10 | 60 | 28 | 85 | NO | 120 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 9 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-R015 | RRG | 600 | 2100 | 1400 |  | 682 | 451 | 0.30758 | 682 | 451 | 0 | 0 | 682 | 682 | 0 | 0 | 451 | 451 | 0 | 0 | 0 | 0 | 682 | 682 | 0 | 0 | 451 | 451 | 0 | 0 | 0.30758 | 700 | 250 | 0 | 0 | 700 | 700 | 0 | 0 | 250 | 250 | 0 | 0 | 0 | NH.RRG | N/A | N/A | N/A | N/A | 0 | N/A | N/A | EC |  | 0.5 | N/A | N/A | Tubular | 6 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 9 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-R025 | RRG | 1300 | 3200 | 2700 |  | 1032 | 581.5 | 0.60011 | 1032 | 581.5 | 0 | 0 | 1032 | 1032 | 0 | 0 | 581.5 | 581.5 | 0 | 0 | 0 | 0 | 1032 | 1032 | 0 | 0 | 581.5 | 581.5 | 0 | 0 | 0.60011 | 1050 | 350 | 0 | 0 | 1050 | 1050 | 0 | 0 | 350 | 350 | 0 | 0 | 0 | NH.RRG | N/A | N/A | N/A | N/A | 0 | N/A | N/A | EC |  | 0.78 | N/A | N/A | Tubular | 9 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 9 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-R035 | RRG | 1800 | 4500 | 3500 |  | 1182 | 640.5 | 0.75707 | 1182 | 640.5 | 0 | 0 | 1182 | 1182 | 0 | 0 | 640.5 | 640.5 | 0 | 0 | 0 | 0 | 1182 | 1182 | 0 | 0 | 640.5 | 640.5 | 0 | 0 | 0.75707 | 1200 | 400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | NH.RRG | N/A | N/A | N/A | N/A | 0 | N/A | N/A | EC |  | 2.4 | N/A | N/A | Tubular | 12 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 9 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-R050 | RRG | 2500 | 7250 | 5000 |  | 1382 | 696 | 0.96187 | 1382 | 696 | 0 | 0 | 1382 | 1382 | 0 | 0 | 696 | 696 | 0 | 0 | 0 | 0 | 1382 | 1382 | 0 | 0 | 696 | 696 | 0 | 0 | 0.96187 | 1400 | 450 | 0 | 0 | 1400 | 1400 | 0 | 0 | 450 | 450 | 0 | 0 | 0 | NH.RRG | N/A | N/A | N/A | N/A | 0 | N/A | N/A | EC |  | 2.5 | N/A | N/A | Tubular | 18 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 9 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-R070 | RRG | 4000 | 9000 | 6900 |  | 1582 | 716 | 1.1327 | 1582 | 716 | 0 | 0 | 1582 | 1582 | 0 | 0 | 716 | 716 | 0 | 0 | 0 | 0 | 1582 | 1582 | 0 | 0 | 716 | 716 | 0 | 0 | 1.1327 | 1600 | 550 | 0 | 0 | 1600 | 1600 | 0 | 0 | 550 | 550 | 0 | 0 | 0 | NH.RRG | N/A | N/A | N/A | N/A | 0 | N/A | N/A | EC |  | 2.5 | N/A | N/A | Tubular | 37 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 9 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-R090 | RRG | 4200 | 11000 | 9000 |  | 1782 | 816 | 1.4541 | 1782 | 816 | 0 | 0 | 1782 | 1782 | 0 | 0 | 816 | 816 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 816 | 816 | 0 | 0 | 1.4541 | 1800 | 650 | 0 | 0 | 1800 | 1800 | 0 | 0 | 650 | 650 | 0 | 0 | 0 | NH.RRG | N/A | N/A | N/A | N/A | 0 | N/A | N/A | EC |  | 3.4 | N/A | N/A | Tubular | 36 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 9 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-R110 | RRG | 5000 | 12700 | 11000 |  | 1982 | 908 | 1.7997 | 1982 | 908 | 0 | 0 | 1982 | 1982 | 0 | 0 | 908 | 908 | 0 | 0 | 0 | 0 | 1982 | 1982 | 0 | 0 | 908 | 908 | 0 | 0 | 1.7997 | 2000 | 750 | 0 | 0 | 2000 | 2000 | 0 | 0 | 750 | 750 | 0 | 0 | 0 | NH.RRG | N/A | N/A | N/A | N/A | 0 | N/A | N/A | EC |  | 3.5 | N/A | N/A | Tubular | 42 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 9 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-R130 | RRG | 7500 | 16600 | 13000 |  | 2082 | 967 | 2.0133 | 2082 | 967 | 0 | 0 | 2082 | 2082 | 0 | 0 | 967 | 967 | 0 | 0 | 0 | 0 | 2082 | 2082 | 0 | 0 | 967 | 967 | 0 | 0 | 2.0133 | 2100 | 800 | 0 | 0 | 2100 | 2100 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | NH.RRG | N/A | N/A | N/A | N/A | 0 | N/A | N/A | EC |  | 4.6 | N/A | N/A | Tubular | 48 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 9 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-R150 | RRG | 8400 | 17500 | 15000 |  | 2182 | 1022 | 2.23 | 2182 | 1022 | 0 | 0 | 2182 | 2182 | 0 | 0 | 1022 | 1022 | 0 | 0 | 0 | 0 | 2182 | 2182 | 0 | 0 | 1022 | 1022 | 0 | 0 | 2.23 | 2200 | 850 | 0 | 0 | 2200 | 2200 | 0 | 0 | 850 | 850 | 0 | 0 | 0 | NH.RRG | N/A | N/A | N/A | N/A | 0 | N/A | N/A | EC |  | 4.6 | N/A | N/A | Tubular | 54 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 6 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-P015 | HEX | 600 | 2000 | 1800 |  | 682 | 479.5 | 0.32702 | 682 | 479.5 | 0 | 0 | 682 | 682 | 0 | 0 | 479.5 | 479.5 | 0 | 0 | 0 | 0 | 682 | 682 | 0 | 0 | 479.5 | 479.5 | 0 | 0 | 0.32702 | 700 | 250 | 0 | 0 | 700 | 700 | 0 | 0 | 250 | 250 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | AL | N/A | N/A | EC |  | 0.5 | N/A | N/A | Tubular | 6 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 6 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-P025 | HEX | 1300 | 3100 | 2900 |  | 1032 | 581.5 | 0.60011 | 1032 | 581.5 | 0 | 0 | 1032 | 1032 | 0 | 0 | 581.5 | 581.5 | 0 | 0 | 0 | 0 | 1032 | 1032 | 0 | 0 | 581.5 | 581.5 | 0 | 0 | 0.60011 | 1050 | 350 | 0 | 0 | 1050 | 1050 | 0 | 0 | 350 | 350 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | AL | N/A | N/A | EC |  | 0.78 | N/A | N/A | Tubular | 9 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 6 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-P035 | HEX | 1800 | 5800 | 4500 |  | 1182 | 640.5 | 0.75707 | 1182 | 640.5 | 0 | 0 | 1182 | 1182 | 0 | 0 | 640.5 | 640.5 | 0 | 0 | 0 | 0 | 1182 | 1182 | 0 | 0 | 640.5 | 640.5 | 0 | 0 | 0.75707 | 1200 | 400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | AL | N/A | N/A | EC |  | 2.4 | N/A | N/A | Tubular | 12 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 6 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-P050 | HEX | 2500 | 7400 | 6600 |  | 1382 | 705 | 0.97431 | 1382 | 705 | 0 | 0 | 1382 | 1382 | 0 | 0 | 705 | 705 | 0 | 0 | 0 | 0 | 1382 | 1382 | 0 | 0 | 705 | 705 | 0 | 0 | 0.97431 | 1400 | 450 | 0 | 0 | 1400 | 1400 | 0 | 0 | 450 | 450 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | AL | N/A | N/A | EC |  | 2.5 | N/A | N/A | Tubular | 18 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 6 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-P070 | HEX | 4000 | 9000 | 8300 |  | 1582 | 849 | 1.3431 | 1582 | 849 | 0 | 0 | 1582 | 1582 | 0 | 0 | 849 | 849 | 0 | 0 | 0 | 0 | 1582 | 1582 | 0 | 0 | 849 | 849 | 0 | 0 | 1.3431 | 1600 | 550 | 0 | 0 | 1600 | 1600 | 0 | 0 | 550 | 550 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | AL | N/A | N/A | EC |  | 2.5 | N/A | N/A | Tubular | 37 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Trox | Trox.png | CER | X-CUBE X2 Compact.png | X-CUBE X2 Compact | Compact | Floor-mounted | 6 | YES | X-CUBE | D1 | L1 | L1 | F9 | T2 | TB2 | Internal declaration | NO | NO | NO | YES | YES | NO | MW | 47 | N/A | N/A | N/A | N/A | X2-P090 | HEX | 4200 | 11000 | 10400 |  | 1782 | 990.5 | 1.7651 | 1782 | 990.5 | 0 | 0 | 1782 | 1782 | 0 | 0 | 990.5 | 990.5 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 990.5 | 990.5 | 0 | 0 | 1.7651 | 1800 | 650 | 0 | 0 | 1800 | 1800 | 0 | 0 | 650 | 650 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | AL | N/A | N/A | EC |  | 3.4 | N/A | N/A | Tubular | 36 | 0 | 0 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Bag | ePM1 | 60 | N/A | N/A | Bag | ePM10 | 60 | N/A | N/A | N/A | 110 | Factory wired
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-10 | RRG | 1000 | 3000 | 2800 | 1.99 | 910 | 432.5 | 0.39358 | 910 | 432.5 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0.39358 | 700 | 300 | 0 | 0 | 700 | 700 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | Condensing | 800 | L | N/A | 74 | 0 | N/A | N/A | EC | 1 | 1.4 | 280 (250) | 72.2 | Tubular | 3 | 12 | 0 | 3 kW step | 1 | 2 | 2 | 4 | 2 | 4 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 124 | 224 | Bag | ePM10 | 60 | 56 | 156 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-10 | RRG | 1000 | 3000 | 2800 | 1.99 | 910 | 432.5 | 0.39358 | 910 | 432.5 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0.39358 | 700 | 300 | 0 | 0 | 700 | 700 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | Condensing | 800 | ML | N/A | 80 | 0 | N/A | N/A | EC | 1 | 1.4 | 280 (250) | 72.2 | Tubular | 3 | 12 | 0 | 3 kW step | 1 | 2 | 2 | 4 | 2 | 4 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 124 | 224 | Bag | ePM10 | 60 | 56 | 156 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-10 | RRG | 1000 | 3000 | 2800 | 1.99 | 910 | 432.5 | 0.39358 | 910 | 432.5 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0.39358 | 700 | 300 | 0 | 0 | 700 | 700 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | Condensing | 800 | SL | N/A | 83 | 0 | N/A | N/A | EC | 1 | 1.4 | 280 (250) | 72.2 | Tubular | 3 | 12 | 0 | 3 kW step | 1 | 2 | 2 | 4 | 2 | 4 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 124 | 224 | Bag | ePM10 | 60 | 56 | 156 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-20 | RRG | 1350 | 5000 | 3800 | 1.97 | 1060 | 507.5 | 0.53795 | 1060 | 507.5 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0.53795 | 900 | 400 | 0 | 0 | 900 | 900 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | 930 | L | N/A | 74 | 0 | N/A | N/A | EC | 1 | 2 | 355 (315) | 73.5 | Tubular | 6 | 30 | 0 | 3 kW step | 1 | 2 | 2 | 4 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 74 | 174 | Bag | ePM10 | 60 | 37 | 112 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-20 | RRG | 1350 | 5000 | 3800 | 1.97 | 1060 | 507.5 | 0.53795 | 1060 | 507.5 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0.53795 | 900 | 400 | 0 | 0 | 900 | 900 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | 930 | ML | N/A | 80 | 0 | N/A | N/A | EC | 1 | 2 | 355 (315) | 73.5 | Tubular | 6 | 30 | 0 | 3 kW step | 1 | 2 | 2 | 4 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 74 | 174 | Bag | ePM10 | 60 | 37 | 112 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-20 | RRG | 1350 | 5000 | 3800 | 1.97 | 1060 | 507.5 | 0.53795 | 1060 | 507.5 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0.53795 | 900 | 400 | 0 | 0 | 900 | 900 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | 930 | SL | N/A | 83 | 0 | N/A | N/A | EC | 1 | 2 | 355 (315) | 73.5 | Tubular | 6 | 30 | 0 | 3 kW step | 1 | 2 | 2 | 4 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 74 | 174 | Bag | ePM10 | 60 | 37 | 112 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-30 | RRG | 1850 | 7000 | 5000 | 1.98 | 1210 | 582.5 | 0.70482 | 1210 | 582.5 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0.70482 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | 1100 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 2.9 | 400 (355) | 75.1 | Tubular | 6 | 36 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 104 | 204 | Bag | ePM10 | 60 | 55 | 155 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-30 | RRG | 1850 | 7000 | 5000 | 1.98 | 1210 | 582.5 | 0.70482 | 1210 | 582.5 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0.70482 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | 1100 | ML | N/A | 81 | 0 | N/A | N/A | EC | 1 | 2.9 | 400 (355) | 75.1 | Tubular | 6 | 36 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 104 | 204 | Bag | ePM10 | 60 | 55 | 155 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-30 | RRG | 1850 | 7000 | 5000 | 1.98 | 1210 | 582.5 | 0.70482 | 1210 | 582.5 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0.70482 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | 1100 | SL | N/A | 84 | 0 | N/A | N/A | EC | 1 | 2.9 | 400 (355) | 75.1 | Tubular | 6 | 36 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 104 | 204 | Bag | ePM10 | 60 | 55 | 155 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-40 | RRG | 2550 | 10000 | 7000 | 2 | 1410 | 692.5 | 0.97642 | 1410 | 692.5 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0.97642 | 1200 | 600 | 0 | 0 | 1200 | 1200 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | 1300 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 2.9 | 450 (400) | 74.8 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 98 | 198 | Bag | ePM10 | 60 | 52 | 152 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-40 | RRG | 2550 | 10000 | 7000 | 2 | 1410 | 692.5 | 0.97642 | 1410 | 692.5 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0.97642 | 1200 | 600 | 0 | 0 | 1200 | 1200 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | 1300 | ML | N/A | 81 | 0 | N/A | N/A | EC | 1 | 2.9 | 450 (400) | 74.8 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 98 | 198 | Bag | ePM10 | 60 | 52 | 152 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-40 | RRG | 2550 | 10000 | 7000 | 2 | 1410 | 692.5 | 0.97642 | 1410 | 692.5 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0.97642 | 1200 | 600 | 0 | 0 | 1200 | 1200 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | 1300 | SL | N/A | 84 | 0 | N/A | N/A | EC | 1 | 2.9 | 450 (400) | 74.8 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 98 | 198 | Bag | ePM10 | 60 | 52 | 152 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-50 | RRG | 3450 | 13000 | 9000 | 1.97 | 1610 | 790 | 1.2719 | 1610 | 790 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 1.2719 | 1400 | 700 | 0 | 0 | 1400 | 1400 | 0 | 0 | 700 | 700 | 0 | 0 | 0 | Condensing | 1500 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 6.6 | 500 (450) | 73.9 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 49 | 146 | Bag | ePM10 | 60 | 36 | 109 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-50 | RRG | 3450 | 13000 | 9000 | 1.97 | 1610 | 790 | 1.2719 | 1610 | 790 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 1.2719 | 1400 | 700 | 0 | 0 | 1400 | 1400 | 0 | 0 | 700 | 700 | 0 | 0 | 0 | Condensing | 1500 | ML | N/A | 81 | 0 | N/A | N/A | EC | 1 | 6.6 | 500 (450) | 73.9 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 49 | 146 | Bag | ePM10 | 60 | 36 | 109 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-50 | RRG | 3450 | 13000 | 9000 | 1.97 | 1610 | 790 | 1.2719 | 1610 | 790 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 1.2719 | 1400 | 700 | 0 | 0 | 1400 | 1400 | 0 | 0 | 700 | 700 | 0 | 0 | 0 | Condensing | 1500 | SL | N/A | 84 | 0 | N/A | N/A | EC | 1 | 6.6 | 500 (450) | 73.9 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 49 | 146 | Bag | ePM10 | 60 | 36 | 109 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-60 | RRG | 4400 | 15500 | 11500 | 1.98 | 1810 | 892.5 | 1.6154 | 1810 | 892.5 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 1.6154 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | 1700 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 7.2 | 560 (500) | 73.4 | Tubular | 12 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 66 | 166 | Bag | ePM10 | 60 | 47 | 140 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-60 | RRG | 4400 | 15500 | 11500 | 1.98 | 1810 | 892.5 | 1.6154 | 1810 | 892.5 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 1.6154 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | 1700 | ML | N/A | 81 | 0 | N/A | N/A | EC | 1 | 7.2 | 560 (500) | 73.4 | Tubular | 12 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 66 | 166 | Bag | ePM10 | 60 | 47 | 140 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-60 | RRG | 4400 | 15500 | 11500 | 1.98 | 1810 | 892.5 | 1.6154 | 1810 | 892.5 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 1.6154 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | 1700 | SL | N/A | 84 | 0 | N/A | N/A | EC | 1 | 7.2 | 560 (500) | 73.4 | Tubular | 12 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 66 | 166 | Bag | ePM10 | 60 | 47 | 140 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-70 | RRG | 5500 | 22000 | 14000 | 1.97 | 2010 | 982.5 | 1.9748 | 2010 | 982.5 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 1.9748 | 1800 | 900 | 0 | 0 | 1800 | 1800 | 0 | 0 | 900 | 900 | 0 | 0 | 0 | Condensing | 1900 | L | N/A | 76 | 0 | N/A | N/A | EC | 1 | 7.2 | 630 (500, 560) | 73.9 | Tubular | 15 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 55 | 155 | Bag | ePM10 | 60 | 40 | 120 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-70 | RRG | 5500 | 22000 | 14000 | 1.97 | 2010 | 982.5 | 1.9748 | 2010 | 982.5 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 1.9748 | 1800 | 900 | 0 | 0 | 1800 | 1800 | 0 | 0 | 900 | 900 | 0 | 0 | 0 | Condensing | 1900 | ML | N/A | 82 | 0 | N/A | N/A | EC | 1 | 7.2 | 630 (500, 560) | 73.9 | Tubular | 15 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 55 | 155 | Bag | ePM10 | 60 | 40 | 120 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-70 | RRG | 5500 | 22000 | 14000 | 1.97 | 2010 | 982.5 | 1.9748 | 2010 | 982.5 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 1.9748 | 1800 | 900 | 0 | 0 | 1800 | 1800 | 0 | 0 | 900 | 900 | 0 | 0 | 0 | Condensing | 1900 | SL | N/A | 84 | 0 | N/A | N/A | EC | 1 | 7.2 | 630 (500, 560) | 73.9 | Tubular | 15 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 55 | 155 | Bag | ePM10 | 60 | 40 | 120 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-80 | RRG | 6800 | 26000 | 18000 | 1.98 | 2210 | 1142.5 | 2.5249 | 2210 | 1142.5 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 2.5249 | 2000 | 1000 | 0 | 0 | 2000 | 2000 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | 2100 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 13.2 | 560 (630) | 74.3 | Tubular | 24 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 59 | 159 | Bag | ePM10 | 60 | 43 | 128 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-80 | RRG | 6800 | 26000 | 18000 | 1.98 | 2210 | 1142.5 | 2.5249 | 2210 | 1142.5 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 2.5249 | 2000 | 1000 | 0 | 0 | 2000 | 2000 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | 2100 | ML | N/A | 81 | 0 | N/A | N/A | EC | 1 | 13.2 | 560 (630) | 74.3 | Tubular | 24 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 59 | 159 | Bag | ePM10 | 60 | 43 | 128 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-80 | RRG | 6800 | 26000 | 18000 | 1.98 | 2210 | 1142.5 | 2.5249 | 2210 | 1142.5 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 2.5249 | 2000 | 1000 | 0 | 0 | 2000 | 2000 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | 2100 | SL | N/A | 84 | 0 | N/A | N/A | EC | 1 | 13.2 | 560 (630) | 74.3 | Tubular | 24 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 59 | 159 | Bag | ePM10 | 60 | 43 | 128 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-90 | RRG | 8800 | 28000 | 22500 | 1.98 | 2520 | 1257.5 | 3.1689 | 2520 | 1257.5 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 3.1689 | 2200 | 1100 | 0 | 0 | 2200 | 2200 | 0 | 0 | 1100 | 1100 | 0 | 0 | 0 | Condensing | 2400 | L | N/A | 76 | 0 | N/A | N/A | EC | 1 | 14.4 | 630 (500, 560) | 75.1 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 53 | 153 | Bag | ePM10 | 60 | 39 | 117 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-90 | RRG | 8800 | 28000 | 22500 | 1.98 | 2520 | 1257.5 | 3.1689 | 2520 | 1257.5 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 3.1689 | 2200 | 1100 | 0 | 0 | 2200 | 2200 | 0 | 0 | 1100 | 1100 | 0 | 0 | 0 | Condensing | 2400 | ML | N/A | 82 | 0 | N/A | N/A | EC | 1 | 14.4 | 630 (500, 560) | 75.1 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 53 | 153 | Bag | ePM10 | 60 | 39 | 117 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-90 | RRG | 8800 | 28000 | 22500 | 1.98 | 2520 | 1257.5 | 3.1689 | 2520 | 1257.5 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 3.1689 | 2200 | 1100 | 0 | 0 | 2200 | 2200 | 0 | 0 | 1100 | 1100 | 0 | 0 | 0 | Condensing | 2400 | SL | N/A | 84 | 0 | N/A | N/A | EC | 1 | 14.4 | 630 (500, 560) | 75.1 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 53 | 153 | Bag | ePM10 | 60 | 39 | 117 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-100 | RRG | 13600 | 40000 | 30000 | 1.98 | 3680 | 1142.5 | 4.2044 | 3680 | 1142.5 | 0 | 0 | 3680 | 3680 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 3680 | 3680 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 4.2044 | 3400 | 1000 | 0 | 0 | 3400 | 3400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | 2*2100 | L | N/A | 77 | 0 | N/A | N/A | EC | 1 | 14.4 | 630 (560) | 73.2 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 60 | 160 | Bag | ePM10 | 60 | 43 | 130 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-100 | RRG | 13600 | 40000 | 30000 | 1.98 | 3680 | 1142.5 | 4.2044 | 3680 | 1142.5 | 0 | 0 | 3680 | 3680 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 3680 | 3680 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 4.2044 | 3400 | 1000 | 0 | 0 | 3400 | 3400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | 2*2100 | ML | N/A | 83 | 0 | N/A | N/A | EC | 1 | 14.4 | 630 (560) | 73.2 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 60 | 160 | Bag | ePM10 | 60 | 43 | 130 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-100 | RRG | 13600 | 40000 | 30000 | 1.98 | 3680 | 1142.5 | 4.2044 | 3680 | 1142.5 | 0 | 0 | 3680 | 3680 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 3680 | 3680 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 4.2044 | 3400 | 1000 | 0 | 0 | 3400 | 3400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | 2*2100 | SL | N/A | 85 | 0 | N/A | N/A | EC | 1 | 14.4 | 630 (560) | 73.2 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 60 | 160 | Bag | ePM10 | 60 | 43 | 130 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-10 | RRG | 1000 | 3000 | 2800 | 1.99 | 910 | 432.5 | 0.39358 | 910 | 432.5 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0.39358 | 700 | 300 | 0 | 0 | 700 | 700 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | Enthalpy | 800 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 1.4 | 280 | 72.2 | Tubular | 3 | 12 | 0 | 3 kW step | 1 | 2 | 2 | 4 | 2 | 4 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 124 | 224 | Bag | ePM10 | 60 | 56 | 156 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-10 | RRG | 1000 | 3000 | 2800 | 1.99 | 910 | 432.5 | 0.39358 | 910 | 432.5 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0.39358 | 700 | 300 | 0 | 0 | 700 | 700 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | Enthalpy | 800 | ML | N/A | 77 | 0 | N/A | N/A | EC | 1 | 1.4 | 280 | 72.2 | Tubular | 3 | 12 | 0 | 3 kW step | 1 | 2 | 2 | 4 | 2 | 4 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 124 | 224 | Bag | ePM10 | 60 | 56 | 156 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-10 | RRG | 1000 | 3000 | 2800 | 1.99 | 910 | 432.5 | 0.39358 | 910 | 432.5 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0.39358 | 700 | 300 | 0 | 0 | 700 | 700 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | Enthalpy | 800 | SL | N/A | 81 | 0 | N/A | N/A | EC | 1 | 1.4 | 280 | 72.2 | Tubular | 3 | 12 | 0 | 3 kW step | 1 | 2 | 2 | 4 | 2 | 4 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 124 | 224 | Bag | ePM10 | 60 | 56 | 156 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-20 | RRG | 1350 | 5000 | 3800 | 1.97 | 1060 | 507.5 | 0.53795 | 1060 | 507.5 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0.53795 | 900 | 400 | 0 | 0 | 900 | 900 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Enthalpy | 930 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 2 | 355 (315) | 73.5 | Tubular | 6 | 30 | 0 | 3 kW step | 1 | 2 | 2 | 4 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 74 | 174 | Bag | ePM10 | 60 | 37 | 112 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-20 | RRG | 1350 | 5000 | 3800 | 1.97 | 1060 | 507.5 | 0.53795 | 1060 | 507.5 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0.53795 | 900 | 400 | 0 | 0 | 900 | 900 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Enthalpy | 930 | ML | N/A | 77 | 0 | N/A | N/A | EC | 1 | 2 | 355 (315) | 73.5 | Tubular | 6 | 30 | 0 | 3 kW step | 1 | 2 | 2 | 4 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 74 | 174 | Bag | ePM10 | 60 | 37 | 112 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-20 | RRG | 1350 | 5000 | 3800 | 1.97 | 1060 | 507.5 | 0.53795 | 1060 | 507.5 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0.53795 | 900 | 400 | 0 | 0 | 900 | 900 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Enthalpy | 930 | SL | N/A | 81 | 0 | N/A | N/A | EC | 1 | 2 | 355 (315) | 73.5 | Tubular | 6 | 30 | 0 | 3 kW step | 1 | 2 | 2 | 4 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 74 | 174 | Bag | ePM10 | 60 | 37 | 112 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-30 | RRG | 1850 | 7000 | 5000 | 1.98 | 1210 | 582.5 | 0.70482 | 1210 | 582.5 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0.70482 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Enthalpy | 1100 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 2.9 | 400 (355) | 75.1 | Tubular | 6 | 36 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 104 | 204 | Bag | ePM10 | 60 | 55 | 155 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-30 | RRG | 1850 | 7000 | 5000 | 1.98 | 1210 | 582.5 | 0.70482 | 1210 | 582.5 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0.70482 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Enthalpy | 1100 | ML | N/A | 77 | 0 | N/A | N/A | EC | 1 | 2.9 | 400 (355) | 75.1 | Tubular | 6 | 36 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 104 | 204 | Bag | ePM10 | 60 | 55 | 155 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-30 | RRG | 1850 | 7000 | 5000 | 1.98 | 1210 | 582.5 | 0.70482 | 1210 | 582.5 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0.70482 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Enthalpy | 1100 | SL | N/A | 81 | 0 | N/A | N/A | EC | 1 | 2.9 | 400 (355) | 75.1 | Tubular | 6 | 36 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 104 | 204 | Bag | ePM10 | 60 | 55 | 155 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-40 | RRG | 2550 | 10000 | 7000 | 2 | 1410 | 692.5 | 0.97642 | 1410 | 692.5 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0.97642 | 1200 | 600 | 0 | 0 | 1200 | 1200 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Enthalpy | 1300 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 2.9 | 450 (400) | 74.8 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 98 | 198 | Bag | ePM10 | 60 | 52 | 152 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-40 | RRG | 2550 | 10000 | 7000 | 2 | 1410 | 692.5 | 0.97642 | 1410 | 692.5 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0.97642 | 1200 | 600 | 0 | 0 | 1200 | 1200 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Enthalpy | 1300 | ML | N/A | 77 | 0 | N/A | N/A | EC | 1 | 2.9 | 450 (400) | 74.8 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 98 | 198 | Bag | ePM10 | 60 | 52 | 152 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-40 | RRG | 2550 | 10000 | 7000 | 2 | 1410 | 692.5 | 0.97642 | 1410 | 692.5 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0.97642 | 1200 | 600 | 0 | 0 | 1200 | 1200 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Enthalpy | 1300 | SL | N/A | 81 | 0 | N/A | N/A | EC | 1 | 2.9 | 450 (400) | 74.8 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 98 | 198 | Bag | ePM10 | 60 | 52 | 152 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-50 | RRG | 3450 | 13000 | 9000 | 1.97 | 1610 | 790 | 1.2719 | 1610 | 790 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 1.2719 | 1400 | 700 | 0 | 0 | 1400 | 1400 | 0 | 0 | 700 | 700 | 0 | 0 | 0 | Enthalpy | 1500 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 6.6 | 500 (450) | 73.9 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 49 | 146 | Bag | ePM10 | 60 | 36 | 109 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-50 | RRG | 3450 | 13000 | 9000 | 1.97 | 1610 | 790 | 1.2719 | 1610 | 790 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 1.2719 | 1400 | 700 | 0 | 0 | 1400 | 1400 | 0 | 0 | 700 | 700 | 0 | 0 | 0 | Enthalpy | 1500 | ML | N/A | 77 | 0 | N/A | N/A | EC | 1 | 6.6 | 500 (450) | 73.9 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 49 | 146 | Bag | ePM10 | 60 | 36 | 109 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-50 | RRG | 3450 | 13000 | 9000 | 1.97 | 1610 | 790 | 1.2719 | 1610 | 790 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 1.2719 | 1400 | 700 | 0 | 0 | 1400 | 1400 | 0 | 0 | 700 | 700 | 0 | 0 | 0 | Enthalpy | 1500 | SL | N/A | 81 | 0 | N/A | N/A | EC | 1 | 6.6 | 500 (450) | 73.9 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 49 | 146 | Bag | ePM10 | 60 | 36 | 109 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-60 | RRG | 4400 | 15500 | 11500 | 1.98 | 1810 | 892.5 | 1.6154 | 1810 | 892.5 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 1.6154 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Enthalpy | 1700 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 7.2 | 560 (500) | 73.4 | Tubular | 12 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 66 | 166 | Bag | ePM10 | 60 | 47 | 140 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-60 | RRG | 4400 | 15500 | 11500 | 1.98 | 1810 | 892.5 | 1.6154 | 1810 | 892.5 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 1.6154 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Enthalpy | 1700 | ML | N/A | 77 | 0 | N/A | N/A | EC | 1 | 7.2 | 560 (500) | 73.4 | Tubular | 12 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 66 | 166 | Bag | ePM10 | 60 | 47 | 140 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-60 | RRG | 4400 | 15500 | 11500 | 1.98 | 1810 | 892.5 | 1.6154 | 1810 | 892.5 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 1.6154 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Enthalpy | 1700 | SL | N/A | 81 | 0 | N/A | N/A | EC | 1 | 7.2 | 560 (500) | 73.4 | Tubular | 12 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 66 | 166 | Bag | ePM10 | 60 | 47 | 140 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-70 | RRG | 5500 | 22000 | 14000 | 1.97 | 2010 | 982.5 | 1.9748 | 2010 | 982.5 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 1.9748 | 1800 | 900 | 0 | 0 | 1800 | 1800 | 0 | 0 | 900 | 900 | 0 | 0 | 0 | Enthalpy | 1900 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 7.2 | 630 (500, 560) | 73.9 | Tubular | 15 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 55 | 155 | Bag | ePM10 | 60 | 40 | 120 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-70 | RRG | 5500 | 22000 | 14000 | 1.97 | 2010 | 982.5 | 1.9748 | 2010 | 982.5 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 1.9748 | 1800 | 900 | 0 | 0 | 1800 | 1800 | 0 | 0 | 900 | 900 | 0 | 0 | 0 | Enthalpy | 1900 | ML | N/A | 77 | 0 | N/A | N/A | EC | 1 | 7.2 | 630 (500, 560) | 73.9 | Tubular | 15 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 55 | 155 | Bag | ePM10 | 60 | 40 | 120 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-70 | RRG | 5500 | 22000 | 14000 | 1.97 | 2010 | 982.5 | 1.9748 | 2010 | 982.5 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 1.9748 | 1800 | 900 | 0 | 0 | 1800 | 1800 | 0 | 0 | 900 | 900 | 0 | 0 | 0 | Enthalpy | 1900 | SL | N/A | 81 | 0 | N/A | N/A | EC | 1 | 7.2 | 630 (500, 560) | 73.9 | Tubular | 15 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 55 | 155 | Bag | ePM10 | 60 | 40 | 120 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-80 | RRG | 6800 | 26000 | 18000 | 1.98 | 2210 | 1142.5 | 2.5249 | 2210 | 1142.5 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 2.5249 | 2000 | 1000 | 0 | 0 | 2000 | 2000 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Enthalpy | 2100 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 13.2 | 560 (630) | 74.3 | Tubular | 24 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 59 | 159 | Bag | ePM10 | 60 | 43 | 128 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-80 | RRG | 6800 | 26000 | 18000 | 1.98 | 2210 | 1142.5 | 2.5249 | 2210 | 1142.5 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 2.5249 | 2000 | 1000 | 0 | 0 | 2000 | 2000 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Enthalpy | 2100 | ML | N/A | 77 | 0 | N/A | N/A | EC | 1 | 13.2 | 560 (630) | 74.3 | Tubular | 24 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 59 | 159 | Bag | ePM10 | 60 | 43 | 128 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-80 | RRG | 6800 | 26000 | 18000 | 1.98 | 2210 | 1142.5 | 2.5249 | 2210 | 1142.5 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 2.5249 | 2000 | 1000 | 0 | 0 | 2000 | 2000 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Enthalpy | 2100 | SL | N/A | 81 | 0 | N/A | N/A | EC | 1 | 13.2 | 560 (630) | 74.3 | Tubular | 24 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 59 | 159 | Bag | ePM10 | 60 | 43 | 128 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-90 | RRG | 8800 | 28000 | 22500 | 1.98 | 2520 | 1257.5 | 3.1689 | 2520 | 1257.5 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 3.1689 | 2200 | 1100 | 0 | 0 | 2200 | 2200 | 0 | 0 | 1100 | 1100 | 0 | 0 | 0 | Enthalpy | 2400 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 14.4 | 630 (500, 560) | 75.1 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 53 | 153 | Bag | ePM10 | 60 | 39 | 117 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-90 | RRG | 8800 | 28000 | 22500 | 1.98 | 2520 | 1257.5 | 3.1689 | 2520 | 1257.5 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 3.1689 | 2200 | 1100 | 0 | 0 | 2200 | 2200 | 0 | 0 | 1100 | 1100 | 0 | 0 | 0 | Enthalpy | 2400 | ML | N/A | 77 | 0 | N/A | N/A | EC | 1 | 14.4 | 630 (500, 560) | 75.1 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 53 | 153 | Bag | ePM10 | 60 | 39 | 117 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-90 | RRG | 8800 | 28000 | 22500 | 1.98 | 2520 | 1257.5 | 3.1689 | 2520 | 1257.5 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 3.1689 | 2200 | 1100 | 0 | 0 | 2200 | 2200 | 0 | 0 | 1100 | 1100 | 0 | 0 | 0 | Enthalpy | 2400 | SL | N/A | 81 | 0 | N/A | N/A | EC | 1 | 14.4 | 630 (500, 560) | 75.1 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 53 | 153 | Bag | ePM10 | 60 | 39 | 117 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-100 | RRG | 13600 | 40000 | 30000 | 1.98 | 3680 | 1142.5 | 4.2044 | 3680 | 1142.5 | 0 | 0 | 3680 | 3680 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 3680 | 3680 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 4.2044 | 3400 | 1000 | 0 | 0 | 3400 | 3400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Enthalpy | 2*2100 | L | N/A | 75 | 0 | N/A | N/A | EC | 1 | 14.4 | 630 (560) | 73.2 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 60 | 160 | Bag | ePM10 | 60 | 43 | 130 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-100 | RRG | 13600 | 40000 | 30000 | 1.98 | 3680 | 1142.5 | 4.2044 | 3680 | 1142.5 | 0 | 0 | 3680 | 3680 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 3680 | 3680 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 4.2044 | 3400 | 1000 | 0 | 0 | 3400 | 3400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Enthalpy | 2*2100 | ML | N/A | 77 | 0 | N/A | N/A | EC | 1 | 14.4 | 630 (560) | 73.2 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 60 | 160 | Bag | ePM10 | 60 | 43 | 130 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso R Pro.png | Verso R Pro | Modular | Floor-mounted | 10 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-100 | RRG | 13600 | 40000 | 30000 | 1.98 | 3680 | 1142.5 | 4.2044 | 3680 | 1142.5 | 0 | 0 | 3680 | 3680 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 3680 | 3680 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 4.2044 | 3400 | 1000 | 0 | 0 | 3400 | 3400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Enthalpy | 2*2100 | SL | N/A | 81 | 0 | N/A | N/A | EC | 1 | 14.4 | 630 (560) | 73.2 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 2 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 60 | 160 | Bag | ePM10 | 60 | 43 | 130 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso CF Pro.png | Verso CF Pro | Modular | Floor-mounted | 9 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-10 | HEX | 1000 | 2500 | 2500 | 1.77 | 910 | 432.5 | 0.39358 | 910 | 432.5 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0 | 0 | 910 | 910 | 0 | 0 | 432.5 | 432.5 | 0 | 0 | 0.39358 | 700 | 300 | 0 | 0 | 700 | 700 | 0 | 0 | 300 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AL 2.1 mm (3 mm) | N/A | 79.6 | EC | 1 | 1.4 | 280 (250) | 72.3 | Tubular | 3 | 12 | 0 | 3 kW step | 1 | 4 | 2 | 4 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 108 | 208 | Bag | ePM10 | 60 | 48 | 143 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso CF Pro.png | Verso CF Pro | Modular | Floor-mounted | 9 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-20 | HEX | 1350 | 3500 | 3500 | 1.82 | 1060 | 507.5 | 0.53795 | 1060 | 507.5 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0 | 0 | 1060 | 1060 | 0 | 0 | 507.5 | 507.5 | 0 | 0 | 0.53795 | 900 | 400 | 0 | 0 | 900 | 900 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AL 2.1 mm (3 mm) | N/A | 79.9 | EC | 1 | 1.4 | 315 (355) | 72.8 | Tubular | 6 | 30 | 0 | 3 kW step | 1 | 4 | 2 | 4 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 67 | 167 | Bag | ePM10 | 60 | 33 | 100 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso CF Pro.png | Verso CF Pro | Modular | Floor-mounted | 9 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-30 | HEX | 1850 | 4400 | 4400 | 1.74 | 1210 | 582.5 | 0.70482 | 1210 | 582.5 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0 | 0 | 1210 | 1210 | 0 | 0 | 582.5 | 582.5 | 0 | 0 | 0.70482 | 1000 | 500 | 0 | 0 | 1000 | 1000 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AL 2.1 mm (3 mm) | N/A | 80.2 | EC | 1 | 2.9 | 400 (355) | 74.4 | Tubular | 6 | 36 | 0 | 3 kW step | 1 | 4 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 89 | 189 | Bag | ePM10 | 60 | 46 | 138 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso CF Pro.png | Verso CF Pro | Modular | Floor-mounted | 9 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-40 | HEX | 2600 | 6700 | 5900 | 1.68 | 1410 | 692.5 | 0.97642 | 1410 | 692.5 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0 | 0 | 1410 | 1410 | 0 | 0 | 692.5 | 692.5 | 0 | 0 | 0.97642 | 1200 | 600 | 0 | 0 | 1200 | 1200 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AL 2.1 mm (3 mm) | N/A | 82 | EC | 1 | 2.9 | 450 (400) | 74.3 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 4 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 93 | 193 | Bag | ePM10 | 60 | 49 | 146 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso CF Pro.png | Verso CF Pro | Modular | Floor-mounted | 9 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-50 | HEX | 3450 | 8400 | 6800 | 1.49 | 1610 | 790 | 1.2719 | 1610 | 790 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 0 | 0 | 1610 | 1610 | 0 | 0 | 790 | 790 | 0 | 0 | 1.2719 | 1400 | 700 | 0 | 0 | 1400 | 1400 | 0 | 0 | 700 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AL 2.1 mm (3 mm) | N/A | 80.9 | EC | 1 | 6.6 | 500 (450) | 74.6 | Tubular | 9 | 45 | 0 | 3 kW step | 1 | 3 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 45 | 135 | Bag | ePM10 | 60 | 34 | 102 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso CF Pro.png | Verso CF Pro | Modular | Floor-mounted | 9 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-60 | HEX | 4400 | 10300 | 9300 | 1.6 | 1810 | 892.5 | 1.6154 | 1810 | 892.5 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 0 | 0 | 1810 | 1810 | 0 | 0 | 892.5 | 892.5 | 0 | 0 | 1.6154 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AL 2.1 mm (3 mm) | N/A | 81 | EC | 1 | 7.2 | 560 (500) | 74.2 | Tubular | 12 | 45 | 0 | 3 kW step | 1 | 3 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 51 | 151 | Bag | ePM10 | 60 | 38 | 113 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso CF Pro.png | Verso CF Pro | Modular | Floor-mounted | 9 | YES | Standart5 | D1 | L1 | L1 | F9 | T2 | TB2 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-70 | HEX | 5500 | 14800 | 13800 | 1.95 | 2010 | 982.5 | 1.9748 | 2010 | 982.5 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 0 | 0 | 2010 | 2010 | 0 | 0 | 982.5 | 982.5 | 0 | 0 | 1.9748 | 1800 | 900 | 0 | 0 | 1800 | 1800 | 0 | 0 | 900 | 900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AL 2.1 mm (3 mm) | N/A | 80 | EC | 1 | 7.2 | 630 (500, 560) | 74.4 | Tubular | 15 | 45 | 0 | 3 kW step | 1 | 3 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 54 | 154 | Bag | ePM10 | 60 | 40 | 119 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso CF Pro.png | Verso CF Pro | Modular | Floor-mounted | 9 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-80 | HEX | 6800 | 18500 | 16300 | 1.8 | 2210 | 1142.5 | 2.5249 | 2210 | 1142.5 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 0 | 0 | 2210 | 2210 | 0 | 0 | 1142.5 | 1142.5 | 0 | 0 | 2.5249 | 2000 | 1000 | 0 | 0 | 2000 | 2000 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AL 2.1 mm (3 mm) | N/A | 81.5 | EC | 1 | 7.2 | 630 (500, 560) | 72.8 | Tubular | 24 | 45 | 0 | 3 kW step | 1 | 3 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 52 | 152 | Bag | ePM10 | 60 | 39 | 116 | N/A | 125 | N/A
Q3 | 2025 | Komfovent | Komfovent.png | CER | Verso CF Pro.png | Verso CF Pro | Modular | Floor-mounted | 9 | YES | Standart2 | D2 | L1 | L1 | F9 | T3 | TB4 | N/A | YES | NO | NO | YES | YES | NO | MW | 45 | Zn | N/A | Zn + Painting (C3 or C4 class) | N/A | PRO-90 | HEX | 8800 | 21610 | 19200 | 1.69 | 2520 | 1257.5 | 3.1689 | 2520 | 1257.5 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 0 | 0 | 2520 | 2520 | 0 | 0 | 1257.5 | 1257.5 | 0 | 0 | 3.1689 | 2200 | 1100 | 0 | 0 | 2200 | 2200 | 0 | 0 | 1100 | 1100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AL 2.1 mm (3 mm) | N/A | 81.3 | EC | 1 | 14.4 | 630 (500, 560) | 73.4 | Tubular | 30 | 45 | 0 | 3 kW step | 1 | 3 | 2 | 3 | 2 | 3 | 1 | R410A, R407C, R32, R404A, R134A, R513A | Bag | ePM1 | 60 | 44 | 131 | Bag | ePM10 | 60 | 33 | 100 | N/A | 125 | N/A
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 4 | RRG | 290 | 1620 | 1200 | 1.22 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Condensing | N/A | STE | N/A | 82.5 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 47 | 140 | Bag | ePM10 | 60 | 18 | 54 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 4 | RRG | 290 | 1620 | 1150 | 1.16 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Condensing | N/A | MTE | N/A | 83.6 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 47 | 140 | Bag | ePM10 | 60 | 18 | 54 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 4 | RRG | 290 | 1620 | 1250 | 1.29 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Condensing | N/A | MPE | N/A | 78.1 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 50 | 149 | Bag | ePM10 | 60 | 19 | 57 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 4 | RRG | 290 | 1620 | 1200 | 1.22 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Sorption | N/A | STE | N/A | 82.2 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 47 | 140 | Bag | ePM10 | 60 | 18 | 54 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 4 | RRG | 290 | 1620 | 1150 | 1.16 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Sorption | N/A | MTE | N/A | 84.7 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 47 | 140 | Bag | ePM10 | 60 | 18 | 54 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 4 | RRG | 290 | 1620 | 1250 | 1.29 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Sorption | N/A | MPE | N/A | 77.8 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 50 | 149 | Bag | ePM10 | 60 | 19 | 57 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 5 | RRG | 290 | 2340 | 1800 | 1.74 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Condensing | N/A | STE | N/A | 78 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 171 | Bag | ePM10 | 60 | 29 | 86 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 5 | RRG | 290 | 2340 | 1700 | 1.63 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 27 | 80 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 5 | RRG | 290 | 2340 | 1800 | 1.74 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Condensing | N/A | MPE | N/A | 73.3 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 171 | Bag | ePM10 | 60 | 29 | 86 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 5 | RRG | 290 | 2340 | 1800 | 1.74 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Sorption | N/A | STE | N/A | 78.9 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 171 | Bag | ePM10 | 60 | 29 | 86 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 5 | RRG | 290 | 2340 | 1600 | 1.54 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Sorption | N/A | MTE | N/A | 82.8 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 27 | 80 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 5 | RRG | 290 | 2340 | 1700 | 1.63 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Sorption | N/A | MPE | N/A | 73.6 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 171 | Bag | ePM10 | 60 | 29 | 86 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 7 | RRG | 290 | 2700 | 2700 | 1.78 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Condensing | N/A | STE | N/A | 79.3 | 0 | N/A | N/A | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 7 | RRG | 290 | 2700 | 2600 | 1.67 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 7 | RRG | 290 | 2700 | 2700 | 1.78 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Condensing | N/A | MPE | N/A | 74.3 | 0 | N/A | N/A | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 7 | RRG | 290 | 2700 | 2700 | 1.78 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Sorption | N/A | STE | N/A | 79.5 | 0 | N/A | N/A | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 7 | RRG | 290 | 2700 | 2600 | 1.67 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Sorption | N/A | MTE | N/A | 82.8 | 0 | N/A | N/A | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 7 | RRG | 290 | 2700 | 2700 | 1.78 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Sorption | N/A | MPE | N/A | 73.9 | 0 | N/A | N/A | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 8 | RRG | 720 | 3600 | 3000 | 1.93 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Condensing | N/A | STE | N/A | 77.7 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 76 | 176 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 8 | RRG | 720 | 3600 | 2800 | 1.79 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 170 | Bag | ePM10 | 60 | 32 | 96 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 8 | RRG | 720 | 3600 | 2800 | 1.79 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Condensing | N/A | MPE | N/A | 73.8 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 170 | Bag | ePM10 | 60 | 32 | 96 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 8 | RRG | 720 | 3600 | 2800 | 1.79 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Sorption | N/A | STE | N/A | 79.3 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 170 | Bag | ePM10 | 60 | 32 | 96 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 8 | RRG | 720 | 3600 | 2600 | 1.67 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Sorption | N/A | MTE | N/A | 82.8 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 170 | Bag | ePM10 | 60 | 32 | 96 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 8 | RRG | 720 | 3600 | 2800 | 1.79 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Sorption | N/A | MPE | N/A | 73.4 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 170 | Bag | ePM10 | 60 | 32 | 96 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 11 | RRG | 750 | 3996 | 3900 | 1.73 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Condensing | N/A | STE | N/A | 79.3 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 11 | RRG | 750 | 3996 | 3900 | 1.73 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 11 | RRG | 750 | 3996 | 3900 | 1.73 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Condensing | N/A | MPE | N/A | 74.9 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 11 | RRG | 750 | 3996 | 3900 | 1.73 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Sorption | N/A | STE | N/A | 79.9 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 11 | RRG | 750 | 3996 | 3700 | 1.62 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Sorption | N/A | MTE | N/A | 83.1 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 11 | RRG | 750 | 3996 | 3900 | 1.73 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Sorption | N/A | MPE | N/A | 74.4 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 12 | RRG | 720 | 5040 | 4200 | 1.85 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Condensing | N/A | STE | N/A | 78.5 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 12 | RRG | 720 | 5040 | 4000 | 1.75 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 12 | RRG | 720 | 5040 | 4200 | 1.85 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Condensing | N/A | MPE | N/A | 73.9 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 12 | RRG | 720 | 5040 | 4000 | 1.75 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Sorption | N/A | STE | N/A | 79.7 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 12 | RRG | 720 | 5040 | 3800 | 1.66 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Sorption | N/A | MTE | N/A | 82.9 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 12 | RRG | 720 | 5040 | 4200 | 1.85 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Sorption | N/A | MPE | N/A | 73.4 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 14 | RRG | 720 | 5940 | 5940 | 2.05 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 78.7 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 14 | RRG | 720 | 5940 | 5600 | 1.91 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 14 | RRG | 720 | 5940 | 5940 | 2.05 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 74 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 14 | RRG | 720 | 5940 | 5940 | 2.05 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | 79.4 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 14 | RRG | 720 | 5940 | 5600 | 1.91 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | 82.8 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 14 | RRG | 720 | 5940 | 5940 | 2.05 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | 73.6 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 20 | RRG | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 78.7 | 0 | N/A | N/A | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 20 | RRG | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 20 | RRG | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 74.1 | 0 | N/A | N/A | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 20 | RRG | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | 79.4 | 0 | N/A | N/A | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 20 | RRG | 1080 | 7560 | 5700 | 1.94 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | 82.7 | 0 | N/A | N/A | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 20 | RRG | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | 73.7 | 0 | N/A | N/A | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 25 | RRG | 1080 | 9000 | 8600 | 1.91 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 77.7 | 0 | N/A | N/A | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 25 | RRG | 1080 | 9000 | 8000 | 1.76 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 25 | RRG | 1080 | 9000 | 8200 | 1.86 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.6 | 0 | N/A | N/A | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 25 | RRG | 1080 | 9000 | 8200 | 1.86 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | 79.1 | 0 | N/A | N/A | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 25 | RRG | 1080 | 9000 | 7200 | 1.59 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | 83 | 0 | N/A | N/A | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 25 | RRG | 1080 | 9000 | 8200 | 1.86 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | 73.1 | 0 | N/A | N/A | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 30 | RRG | 1800 | 11520 | 8500 | 1.89 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 77.9 | 0 | N/A | N/A | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 30 | RRG | 1800 | 11520 | 8000 | 1.76 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 30 | RRG | 1800 | 11520 | 8500 | 1.89 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.1 | 0 | N/A | N/A | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 30 | RRG | 1800 | 11520 | 8200 | 1.86 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | 79.1 | 0 | N/A | N/A | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 30 | RRG | 1800 | 11520 | 7500 | 1.65 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | 82.8 | 0 | N/A | N/A | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 30 | RRG | 1800 | 11520 | 8200 | 1.86 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | 73.1 | 0 | N/A | N/A | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 35 | RRG | 1800 | 14400 | 12900 | 2.09 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 78.4 | 0 | N/A | N/A | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 35 | RRG | 1800 | 14400 | 12300 | 1.98 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 35 | RRG | 1800 | 14400 | 12900 | 2.09 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.8 | 0 | N/A | N/A | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 35 | RRG | 1800 | 14400 | 12900 | 2.09 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 35 | RRG | 1800 | 14400 | 12300 | 1.98 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 35 | RRG | 1800 | 14400 | 12900 | 2.09 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 40 | RRG | 2520 | 18000 | 13000 | 2.11 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 78.4 | 0 | N/A | N/A | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 40 | RRG | 2520 | 18000 | 12200 | 1.96 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 40 | RRG | 2520 | 18000 | 13000 | 2.11 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.7 | 0 | N/A | N/A | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 40 | RRG | 2520 | 18000 | 13000 | 2.11 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 40 | RRG | 2520 | 18000 | 12200 | 1.96 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 40 | RRG | 2520 | 18000 | 13000 | 2.11 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 50 | RRG | 2520 | 18000 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 77.9 | 0 | N/A | N/A | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 50 | RRG | 2520 | 18000 | 16500 | 1.82 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 50 | RRG | 2520 | 18000 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.5 | 0 | N/A | N/A | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 50 | RRG | 2520 | 18000 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 50 | RRG | 2520 | 18000 | 16500 | 1.82 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 50 | RRG | 2520 | 18000 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 60 | RRG | 3600 | 23400 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 77.9 | 0 | N/A | N/A | EC | 2 | 4 | 60 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 60 | RRG | 3600 | 23400 | 16500 | 1.82 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 2 | 4 | 60 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 60 | RRG | 3600 | 23400 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.5 | 0 | N/A | N/A | EC | 2 | 4 | 60 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 60 | RRG | 3600 | 23400 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 4 | 60 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 60 | RRG | 3600 | 23400 | 16500 | 1.82 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 4 | 60 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 60 | RRG | 3600 | 23400 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 4 | 60 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 70 | RRG | 3600 | 28800 | 25000 | 2.39 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 77.5 | 0 | N/A | N/A | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 70 | RRG | 3600 | 28800 | 23000 | 2.19 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 70 | RRG | 3600 | 28800 | 23000 | 2.19 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.8 | 0 | N/A | N/A | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 70 | RRG | 3600 | 28800 | 25000 | 2.39 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 70 | RRG | 3600 | 28800 | 23000 | 2.19 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 70 | RRG | 3600 | 28800 | 23000 | 2.19 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 80 | RRG | 5040 | 34200 | 24500 | 2.35 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 77.8 | 0 | N/A | N/A | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 80 | RRG | 5040 | 34200 | 22000 | 2.1 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 80 | RRG | 5040 | 34200 | 24000 | 2.34 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.3 | 0 | N/A | N/A | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 80 | RRG | 5040 | 34200 | 24500 | 2.35 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 80 | RRG | 5040 | 34200 | 22000 | 2.1 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 80 | RRG | 5040 | 34200 | 24000 | 2.34 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 100 | RRG | 5400 | 39600 | 37500 | 2.26 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 78.4 | 0 | N/A | N/A | EC | 2 | 10 (6,5) | 100 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 109 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 100 | RRG | 5400 | 39600 | 35000 | 2.1 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 2 | 10 (6,5) | 100 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 109 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 100 | RRG | 5400 | 39600 | 36000 | 2.21 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 74.3 | 0 | N/A | N/A | EC | 2 | 10 (6,5) | 100 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 109 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 100 | RRG | 5400 | 39600 | 37500 | 2.26 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 10 (6,5) | 100 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 109 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 100 | RRG | 5400 | 39600 | 35000 | 2.1 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 10 (6,5) | 100 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 109 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 100 | RRG | 5400 | 39600 | 36000 | 2.21 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 10 (6,5) | 100 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 109 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 120 | RRG | 9000 | 50400 | 36000 | 2.21 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 78.8 | 0 | N/A | N/A | EC | 3 | 6.5 | 120 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 74 | 174 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 120 | RRG | 9000 | 50400 | 34000 | 2.04 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.9 | 0 | N/A | N/A | EC | 3 | 6.5 | 120 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 74 | 174 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 120 | RRG | 9000 | 50400 | 35000 | 2.16 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 74.6 | 0 | N/A | N/A | EC | 3 | 6.5 | 120 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 74 | 174 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 120 | RRG | 9000 | 50400 | 36000 | 2.21 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 3 | 6.5 | 120 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 74 | 174 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 120 | RRG | 9000 | 50400 | 34000 | 2.04 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 3 | 6.5 | 120 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 74 | 174 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F RX.png | Gold F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 120 | RRG | 9000 | 50400 | 35000 | 2.16 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 3 | 6.5 | 120 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 74 | 174 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 4 | HEX | 290 | 1620 | 1350 | 1.2 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 75.3 | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 47 | 140 | Bag | ePM10 | 60 | 18 | 54 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 4 | HEX | 290 | 1620 | 1300 | 1.16 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.7 | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 47 | 140 | Bag | ePM10 | 60 | 18 | 54 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 5 | HEX | 290 | 2340 | 1800 | 1.74 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 73.6 | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 171 | Bag | ePM10 | 60 | 29 | 86 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 5 | HEX | 290 | 2340 | 1800 | 1.74 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 80.6 | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 171 | Bag | ePM10 | 60 | 29 | 86 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 7 | HEX | 290 | 2700 | 2600 | 1.56 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 73.9 | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 7 | HEX | 290 | 2700 | 2600 | 1.56 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.2 | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 8 | HEX | 720 | 3600 | 2900 | 1.74 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 73.3 | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 76 | 176 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 8 | HEX | 720 | 3600 | 2900 | 1.74 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 81.6 | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 76 | 176 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 11 | HEX | 750 | 3996 | 3900 | 1.6 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 76.7 | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 11 | HEX | 750 | 3996 | 3900 | 1.6 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.2 | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 12 | HEX | 720 | 5040 | 3900 | 1.6 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 76.7 | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 12 | HEX | 720 | 5040 | 3900 | 1.6 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.2 | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 14 | HEX | 720 | 5940 | 5940 | 2.05 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 74.4 | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 14 | HEX | 720 | 5940 | 5940 | 2.05 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 81.7 | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 20 | HEX | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 74.4 | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 20 | HEX | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 81.7 | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 25 | HEX | 1080 | 9000 | 8600 | 1.91 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 74.3 | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 25 | HEX | 1080 | 9000 | 8600 | 1.91 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.5 | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 30 | HEX | 1800 | 11520 | 8500 | 1.89 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 74.4 | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 30 | HEX | 1800 | 11520 | 8500 | 1.89 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.6 | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 35 | HEX | 1800 | 14400 | 12800 | 1.94 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 77.3 | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 35 | HEX | 1800 | 14400 | 12800 | 1.94 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.5 | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 40 | HEX | 2520 | 18000 | 13000 | 2.11 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 77.2 | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 40 | HEX | 2520 | 18000 | 13000 | 2.11 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.4 | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 50+ | HEX | 2520 | 21600 | 17000 | 1.78 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 78.5 | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 50+ | HEX | 2520 | 21600 | 17000 | 1.78 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.2 | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 70 | HEX | 3600 | 28800 | 24000 | 2.17 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 80.3 | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Gold F PX.png | Gold F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 80 | HEX | 5040 | 34200 | 23500 | 2.13 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 80.4 | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | Factory wired
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 4 | RRG | 290 | 1620 | 1200 | 1.22 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Condensing | N/A | STE | N/A | 82.5 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 47 | 140 | Bag | ePM10 | 60 | 18 | 54 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 4 | RRG | 290 | 1620 | 1150 | 1.16 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Condensing | N/A | MTE | N/A | 83.6 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 47 | 140 | Bag | ePM10 | 60 | 18 | 54 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 4 | RRG | 290 | 1620 | 1250 | 1.29 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Condensing | N/A | MPE | N/A | 78.1 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 50 | 149 | Bag | ePM10 | 60 | 19 | 57 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 4 | RRG | 290 | 1620 | 1200 | 1.22 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Sorption | N/A | STE | N/A | 82.2 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 47 | 140 | Bag | ePM10 | 60 | 18 | 54 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 4 | RRG | 290 | 1620 | 1150 | 1.16 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Sorption | N/A | MTE | N/A | 84.7 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 47 | 140 | Bag | ePM10 | 60 | 18 | 54 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 4 | RRG | 290 | 1620 | 1250 | 1.29 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Sorption | N/A | MPE | N/A | 77.8 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 50 | 149 | Bag | ePM10 | 60 | 19 | 57 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 5 | RRG | 290 | 2340 | 1800 | 1.74 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Condensing | N/A | STE | N/A | 78 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 171 | Bag | ePM10 | 60 | 29 | 86 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 5 | RRG | 290 | 2340 | 1700 | 1.63 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 27 | 80 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 5 | RRG | 290 | 2340 | 1800 | 1.74 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Condensing | N/A | MPE | N/A | 73.3 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 171 | Bag | ePM10 | 60 | 29 | 86 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 5 | RRG | 290 | 2340 | 1800 | 1.74 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Sorption | N/A | STE | N/A | 78.9 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 171 | Bag | ePM10 | 60 | 29 | 86 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 5 | RRG | 290 | 2340 | 1600 | 1.54 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Sorption | N/A | MTE | N/A | 82.8 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 27 | 80 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 5 | RRG | 290 | 2340 | 1700 | 1.63 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | Sorption | N/A | MPE | N/A | 73.6 | 0 | N/A | N/A | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 171 | Bag | ePM10 | 60 | 29 | 86 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 7 | RRG | 290 | 2700 | 2700 | 1.78 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Condensing | N/A | STE | N/A | 79.3 | 0 | N/A | N/A | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 7 | RRG | 290 | 2700 | 2600 | 1.67 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 7 | RRG | 290 | 2700 | 2700 | 1.78 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Condensing | N/A | MPE | N/A | 74.3 | 0 | N/A | N/A | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 7 | RRG | 290 | 2700 | 2700 | 1.78 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Sorption | N/A | STE | N/A | 79.5 | 0 | N/A | N/A | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 7 | RRG | 290 | 2700 | 2600 | 1.67 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Sorption | N/A | MTE | N/A | 82.8 | 0 | N/A | N/A | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 7 | RRG | 290 | 2700 | 2700 | 1.78 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Sorption | N/A | MPE | N/A | 73.9 | 0 | N/A | N/A | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 8 | RRG | 720 | 3600 | 3000 | 1.93 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Condensing | N/A | STE | N/A | 77.7 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 76 | 176 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 8 | RRG | 720 | 3600 | 2800 | 1.79 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 170 | Bag | ePM10 | 60 | 32 | 96 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 8 | RRG | 720 | 3600 | 2800 | 1.79 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Condensing | N/A | MPE | N/A | 73.8 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 170 | Bag | ePM10 | 60 | 32 | 96 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 8 | RRG | 720 | 3600 | 2800 | 1.79 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Sorption | N/A | STE | N/A | 79.3 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 170 | Bag | ePM10 | 60 | 32 | 96 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 8 | RRG | 720 | 3600 | 2600 | 1.67 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Sorption | N/A | MTE | N/A | 82.8 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 170 | Bag | ePM10 | 60 | 32 | 96 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 8 | RRG | 720 | 3600 | 2800 | 1.79 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | Sorption | N/A | MPE | N/A | 73.4 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 170 | Bag | ePM10 | 60 | 32 | 96 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 11 | RRG | 750 | 3996 | 3900 | 1.73 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Condensing | N/A | STE | N/A | 79.3 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 11 | RRG | 750 | 3996 | 3900 | 1.73 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 11 | RRG | 750 | 3996 | 3900 | 1.73 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Condensing | N/A | MPE | N/A | 74.9 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 11 | RRG | 750 | 3996 | 3900 | 1.73 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Sorption | N/A | STE | N/A | 79.9 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 11 | RRG | 750 | 3996 | 3700 | 1.62 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Sorption | N/A | MTE | N/A | 83.1 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 11 | RRG | 750 | 3996 | 3900 | 1.73 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Sorption | N/A | MPE | N/A | 74.4 | 0 | N/A | N/A | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 12 | RRG | 720 | 5040 | 4200 | 1.85 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Condensing | N/A | STE | N/A | 78.5 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 12 | RRG | 720 | 5040 | 4000 | 1.75 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 12 | RRG | 720 | 5040 | 4200 | 1.85 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Condensing | N/A | MPE | N/A | 73.9 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 12 | RRG | 720 | 5040 | 4000 | 1.75 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Sorption | N/A | STE | N/A | 79.7 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 12 | RRG | 720 | 5040 | 3800 | 1.66 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Sorption | N/A | MTE | N/A | 82.9 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 12 | RRG | 720 | 5040 | 4200 | 1.85 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | Sorption | N/A | MPE | N/A | 73.4 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 14 | RRG | 720 | 5940 | 5940 | 2.05 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 78.7 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 14 | RRG | 720 | 5940 | 5600 | 1.91 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 14 | RRG | 720 | 5940 | 5940 | 2.05 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 74 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 14 | RRG | 720 | 5940 | 5940 | 2.05 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | 79.4 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 14 | RRG | 720 | 5940 | 5600 | 1.91 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | 82.8 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 14 | RRG | 720 | 5940 | 5940 | 2.05 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | 73.6 | 0 | N/A | N/A | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 20 | RRG | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 78.7 | 0 | N/A | N/A | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 20 | RRG | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 20 | RRG | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 74.1 | 0 | N/A | N/A | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 20 | RRG | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | 79.4 | 0 | N/A | N/A | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 20 | RRG | 1080 | 7560 | 5700 | 1.94 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | 82.7 | 0 | N/A | N/A | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 20 | RRG | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | 73.7 | 0 | N/A | N/A | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 25 | RRG | 1080 | 9000 | 8600 | 1.91 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 77.7 | 0 | N/A | N/A | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 25 | RRG | 1080 | 9000 | 8000 | 1.76 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 25 | RRG | 1080 | 9000 | 8200 | 1.86 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.6 | 0 | N/A | N/A | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 25 | RRG | 1080 | 9000 | 8200 | 1.86 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | 79.1 | 0 | N/A | N/A | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 25 | RRG | 1080 | 9000 | 7200 | 1.59 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | 83 | 0 | N/A | N/A | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 25 | RRG | 1080 | 9000 | 8200 | 1.86 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | 73.1 | 0 | N/A | N/A | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 30 | RRG | 1800 | 11520 | 8500 | 1.89 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 77.9 | 0 | N/A | N/A | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 30 | RRG | 1800 | 11520 | 8000 | 1.76 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 30 | RRG | 1800 | 11520 | 8500 | 1.89 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.1 | 0 | N/A | N/A | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 30 | RRG | 1800 | 11520 | 8200 | 1.86 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | 79.1 | 0 | N/A | N/A | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 30 | RRG | 1800 | 11520 | 7500 | 1.65 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | 82.8 | 0 | N/A | N/A | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 30 | RRG | 1800 | 11520 | 8200 | 1.86 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | 73.1 | 0 | N/A | N/A | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 35 | RRG | 1800 | 14400 | 12900 | 2.09 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 78.4 | 0 | N/A | N/A | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 35 | RRG | 1800 | 14400 | 12300 | 1.98 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 35 | RRG | 1800 | 14400 | 12900 | 2.09 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.8 | 0 | N/A | N/A | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 35 | RRG | 1800 | 14400 | 12900 | 2.09 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 35 | RRG | 1800 | 14400 | 12300 | 1.98 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 35 | RRG | 1800 | 14400 | 12900 | 2.09 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 40 | RRG | 2520 | 18000 | 13000 | 2.11 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 78.4 | 0 | N/A | N/A | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 40 | RRG | 2520 | 18000 | 12200 | 1.96 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 40 | RRG | 2520 | 18000 | 13000 | 2.11 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.7 | 0 | N/A | N/A | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 40 | RRG | 2520 | 18000 | 13000 | 2.11 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 40 | RRG | 2520 | 18000 | 12200 | 1.96 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 40 | RRG | 2520 | 18000 | 13000 | 2.11 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 50 | RRG | 2520 | 18000 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 77.9 | 0 | N/A | N/A | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 50 | RRG | 2520 | 18000 | 16500 | 1.82 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 50 | RRG | 2520 | 18000 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.5 | 0 | N/A | N/A | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 50 | RRG | 2520 | 18000 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 50 | RRG | 2520 | 18000 | 16500 | 1.82 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 50 | RRG | 2520 | 18000 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 60 | RRG | 3600 | 23400 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 77.9 | 0 | N/A | N/A | EC | 2 | 4 | 60 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 60 | RRG | 3600 | 23400 | 16500 | 1.82 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 2 | 4 | 60 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 60 | RRG | 3600 | 23400 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.5 | 0 | N/A | N/A | EC | 2 | 4 | 60 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 60 | RRG | 3600 | 23400 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 4 | 60 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 60 | RRG | 3600 | 23400 | 16500 | 1.82 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 4 | 60 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 60 | RRG | 3600 | 23400 | 17500 | 1.95 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 4 | 60 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 70 | RRG | 3600 | 28800 | 25000 | 2.39 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 77.5 | 0 | N/A | N/A | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 70 | RRG | 3600 | 28800 | 23000 | 2.19 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.7 | 0 | N/A | N/A | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 70 | RRG | 3600 | 28800 | 23000 | 2.19 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.8 | 0 | N/A | N/A | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 70 | RRG | 3600 | 28800 | 25000 | 2.39 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 70 | RRG | 3600 | 28800 | 23000 | 2.19 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 70 | RRG | 3600 | 28800 | 23000 | 2.19 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 80 | RRG | 5040 | 34200 | 24500 | 2.35 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 77.8 | 0 | N/A | N/A | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 80 | RRG | 5040 | 34200 | 22000 | 2.1 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 80 | RRG | 5040 | 34200 | 24000 | 2.34 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 73.3 | 0 | N/A | N/A | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 80 | RRG | 5040 | 34200 | 24500 | 2.35 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 80 | RRG | 5040 | 34200 | 22000 | 2.1 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 80 | RRG | 5040 | 34200 | 24000 | 2.34 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 100 | RRG | 5400 | 39600 | 37500 | 2.26 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 78.4 | 0 | N/A | N/A | EC | 2 | 10 (6,5) | 100 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 109 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 100 | RRG | 5400 | 39600 | 35000 | 2.1 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.8 | 0 | N/A | N/A | EC | 2 | 10 (6,5) | 100 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 109 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 100 | RRG | 5400 | 39600 | 36000 | 2.21 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 74.3 | 0 | N/A | N/A | EC | 2 | 10 (6,5) | 100 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 109 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 100 | RRG | 5400 | 39600 | 37500 | 2.26 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 10 (6,5) | 100 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 109 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 100 | RRG | 5400 | 39600 | 35000 | 2.1 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 10 (6,5) | 100 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 109 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 100 | RRG | 5400 | 39600 | 36000 | 2.21 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 2 | 10 (6,5) | 100 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 109 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 120 | RRG | 9000 | 50400 | 36000 | 2.21 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Condensing | N/A | STE | N/A | 78.8 | 0 | N/A | N/A | EC | 3 | 6.5 | 120 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 74 | 174 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 120 | RRG | 9000 | 50400 | 34000 | 2.04 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Condensing | N/A | MTE | N/A | 81.9 | 0 | N/A | N/A | EC | 3 | 6.5 | 120 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 74 | 174 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 120 | RRG | 9000 | 50400 | 35000 | 2.16 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Condensing | N/A | MPE | N/A | 74.6 | 0 | N/A | N/A | EC | 3 | 6.5 | 120 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 74 | 174 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 120 | RRG | 9000 | 50400 | 36000 | 2.21 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Sorption | N/A | STE | N/A | N/A | 0 | N/A | N/A | EC | 3 | 6.5 | 120 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 74 | 174 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 120 | RRG | 9000 | 50400 | 34000 | 2.04 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Sorption | N/A | MTE | N/A | N/A | 0 | N/A | N/A | EC | 3 | 6.5 | 120 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 74 | 174 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F RX.png | Silver F RX | Compact | Floor-mounted | 20 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F RX 120 | RRG | 9000 | 50400 | 35000 | 2.16 | 3236 | 1592 | 5.1517 | 3132 | 718 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 0 | 0 | 3132 | 3132 | 0 | 0 | 718 | 718 | 0 | 0 | 5.1517 | 2400 | 1200 | 0 | 0 | 2400 | 2400 | 0 | 0 | 1200 | 1200 | 0 | 0 | 0 | Sorption | N/A | MPE | N/A | N/A | 0 | N/A | N/A | EC | 3 | 6.5 | 120 | N/A | Tubular | 42 | 60 | 90 | 42; 60; 90; 141 | 1 | 3 | 3 | 4 | N/A | N/A | 1-4 | R32 | Bag | ePM1 | 50 | 74 | 174 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 4 | HEX | 290 | 1620 | 1350 | 1.2 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 75.3 | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 47 | 140 | Bag | ePM10 | 60 | 18 | 54 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 4 | HEX | 290 | 1620 | 1300 | 1.16 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.7 | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 2 | 3 | 1-2 | R32 | Bag | ePM1 | 50 | 47 | 140 | Bag | ePM10 | 60 | 18 | 54 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 5 | HEX | 290 | 2340 | 1800 | 1.74 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 73.6 | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 171 | Bag | ePM10 | 60 | 29 | 86 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 5 | HEX | 290 | 2340 | 1800 | 1.74 | 721 | 382 | 0.27542 | 617 | 113 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0 | 0 | 617 | 617 | 0 | 0 | 113 | 113 | 0 | 0 | 0.27542 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 80.6 | EC | 1 | 0.8 | N/A | N/A | Tubular | 2.5 | 4.5 | 7.5 | 2,5; 4,5; 7,5; 10,2 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 70 | 171 | Bag | ePM10 | 60 | 29 | 86 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 7 | HEX | 290 | 2700 | 2600 | 1.56 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 73.9 | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 7 | HEX | 290 | 2700 | 2600 | 1.56 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.2 | EC | 1 | 1.15 (0.8) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 6 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 65 | 165 | Bag | ePM10 | 60 | 59 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 8 | HEX | 720 | 3600 | 2900 | 1.74 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 73.3 | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 76 | 176 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 8 | HEX | 720 | 3600 | 2900 | 1.74 | 891 | 464.5 | 0.41387 | 787 | 154.25 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0 | 0 | 787 | 787 | 0 | 0 | 154.25 | 154.25 | 0 | 0 | 0.41387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 81.6 | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 4.5 | 7.5 | 12 | 4,5; 7,5; 12; 18 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 76 | 176 | Bag | ePM10 | 60 | 35 | 104 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 11 | HEX | 750 | 3996 | 3900 | 1.6 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 76.7 | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 11 | HEX | 750 | 3996 | 3900 | 1.6 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.2 | EC | 1 | 1.6 (1.15) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 6 | 3 | 4 | 1-2 | R32 | Bag | ePM1 | 50 | 84 | 184 | Bag | ePM10 | 60 | 42 | 126 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 12 | HEX | 720 | 5040 | 3900 | 1.6 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 76.7 | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 12 | HEX | 720 | 5040 | 3900 | 1.6 | 1095 | 569.5 | 0.6236 | 991 | 206.75 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0 | 0 | 991 | 991 | 0 | 0 | 206.75 | 206.75 | 0 | 0 | 0.6236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.2 | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 6 | 10.2 | 21 | 6; 10,2; 21; 30; 42 | 1 | 3 | 4 | 10 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 91 | 192 | Bag | ePM10 | 60 | 46 | 138 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 14 | HEX | 720 | 5940 | 5940 | 2.05 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 74.4 | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 14 | HEX | 720 | 5940 | 5940 | 2.05 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 81.7 | EC | 1 | 2.4 (1.6) | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 5 | 1-2 | R32 | Bag | ePM1 | 50 | 78 | 178 | Bag | ePM10 | 60 | 36 | 107 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 20 | HEX | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 74.4 | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 20 | HEX | 1080 | 7560 | 5900 | 2.04 | 1296 | 697.5 | 0.90396 | 1192 | 270.75 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0 | 0 | 1192 | 1192 | 0 | 0 | 270.75 | 270.75 | 0 | 0 | 0.90396 | 1000 | 400 | 0 | 0 | 1000 | 1000 | 0 | 0 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 81.7 | EC | 1 | 2.4 | N/A | N/A | Tubular | 10.2 | 15 | 27 | 10.2; 15; 27; 42; 51 | 1 | 3 | 4 | 8 | 3 | 6 | 1-2 | R32 | Bag | ePM1 | 50 | 77 | 177 | Bag | ePM10 | 60 | 71 | 106 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 25 | HEX | 1080 | 9000 | 8600 | 1.91 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 74.3 | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 25 | HEX | 1080 | 9000 | 8600 | 1.91 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.5 | EC | 1 | 3.4 (2.4) | 25 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 63 | 163 | Bag | ePM10 | 60 | 29 | 88 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 30 | HEX | 1800 | 11520 | 8500 | 1.89 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 74.4 | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 30 | HEX | 1800 | 11520 | 8500 | 1.89 | 1496 | 827.5 | 1.2379 | 1392 | 335.75 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 0 | 0 | 1392 | 1392 | 0 | 0 | 335.75 | 335.75 | 0 | 0 | 1.2379 | 1200 | 500 | 0 | 0 | 1200 | 1200 | 0 | 0 | 500 | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.6 | EC | 1 | 4 (5) | 30 | N/A | Tubular | 15 | 21 | 33 | 15; 21; 33; 45; 66 | 1 | 3 | 4 | 8 | 3 | 4 | 1-4 | R32 | Bag | ePM1 | 50 | 62 | 162 | Bag | ePM10 | 60 | 29 | 87 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 35 | HEX | 1800 | 14400 | 12800 | 1.94 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 77.3 | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 35 | HEX | 1800 | 14400 | 12800 | 1.94 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.5 | EC | 1 | 5 (4) | 35 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 40 | HEX | 2520 | 18000 | 13000 | 2.11 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 77.2 | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 40 | HEX | 2520 | 18000 | 13000 | 2.11 | 1886 | 1001.5 | 1.8888 | 1782 | 422.75 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 0 | 0 | 1782 | 1782 | 0 | 0 | 422.75 | 422.75 | 0 | 0 | 1.8888 | 1400 | 600 | 0 | 0 | 1400 | 1400 | 0 | 0 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.4 | EC | 1 | 6.5 | 40 | N/A | Tubular | 21 | 27 | 42 | 21; 27; 42; 60; 84 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 50+ | HEX | 2520 | 21600 | 17000 | 1.78 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 78.5 | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 50+ | HEX | 2520 | 21600 | 17000 | 1.78 | 2214 | 1066 | 2.3601 | 2110 | 455 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 0 | 0 | 2110 | 2110 | 0 | 0 | 455 | 455 | 0 | 0 | 2.3601 | 1600 | 800 | 0 | 0 | 1600 | 1600 | 0 | 0 | 800 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MTE | N/A | 82.2 | EC | 1 | 10 (6.5) | 50 | N/A | Tubular | 27 | 42 | 57 | 27; 42; 57; 78; 99 | 1 | 3 | 4 | 8 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 75 | 175 | Bag | ePM10 | 60 | 35 | 105 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 70 | HEX | 3600 | 28800 | 24000 | 2.17 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 80.3 | EC | 2 | 6,5 (4) | 70 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO
Q3 | 2025 | Swegon | Swegon.png | CER | Silver F PX.png | Silver F PX | Compact | Floor-mounted | 17 | YES | Version F casing 3 | D1 | L1 | L2 | F9 | T2 | TB2 | YES | YES | YES | NO | YES | YES | YES | MW | 52 | Zn | 1 | Zn + Painting (C3 or C4 class) | 1 | F PX 80 | HEX | 5040 | 34200 | 23500 | 2.13 | 2533 | 1242 | 3.146 | 2429 | 543 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 0 | 0 | 2429 | 2429 | 0 | 0 | 543 | 543 | 0 | 0 | 3.146 | 1800 | 1000 | 0 | 0 | 1800 | 1800 | 0 | 0 | 1000 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Al_MPE | N/A | 80.4 | EC | 2 | 6.5 | 80 | N/A | Tubular | 42 | 57 | 78 | 42; 57; 78; 99 | 1 | 3 | 3 | 5 | 3 | 5 | 1-4 | R32 | Bag | ePM1 | 50 | 81 | 181 | Bag | ePM10 | 60 | 38 | 114 | N/A | 100 | NO